[image: image1.png]P
o w
E R
S O
1C IONS///,





Molded Machine Tool Rated
Control Transformer

Typical Specification

Canada
595 Southgate Drive

Guelph, Ontario
N1G 3W6
Phone: 1-888-798-8882
Fax: 1-519-822-9701
United States
1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

1 GENERAL

1.1 SCOPE

A This section defines molded, machine tool rated control transformer as indicated.
B Transformers shall be designed, constructed and rated in accordance with NEMA ST-1, UL 5085-1 and UL5085-2, CSA C22.2 No. 66.1-06 and IEC 61558 standards. 

1.2 RELATED DOCUMENTS

A Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.
1.3 REFERENCES

A UL (ANSI/UL 5085-1 & ANSI/UL 5085-2)
B cULus

C CSA (C22.2 No. 66.1-06)

D NEMA (ST-1) 

E IEC 61558-1 & IEC61558-2-2
1.4 SUBMITALS

A Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract. 

i Customer name, Customer location, and customer order number, shall identify all transmittals.

ii Product Data including VA rating, temperature rise, detailed dimensions, primary & secondary nominal voltages, primary & secondary voltage taps, inrush, unit weight, warranty.
1.5 STORAGE AND HANDLING

A Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations.
B Handle transformer using proper equipment for lifting and handling.

1.6 WARRANTY

A The transformer shall carry a lifetime limited warranty.
(For details, refer to the manufacturers published warranty)
2 PRODUCTS

2.1 General construction:

A Single phase machine tool control transformers shall be molded. All single phase transformers shall be constructed with copper wound coils and a single core. 

B Transformers shall be designed, constructed and rated in accordance with UL, CSA, NEMA and CE standards.

2.2 Voltage and VA Requirements:

A Primary & Secondary Voltage combinations: 

             [600-120x240][600-24][277/208-120x240][240x480-120x240][240x480-24][208x416-120x240]
             [120x240-120x240][120x240-24][575/460/230-115/95][460/230/208-115/24]

             [415/400/380-110x220][380/277/208-120x240][575/460/400/230-115/24][other] Volts
B VA Rating: [50][75][100][150][250][350][500][750][1000][1500][2000][other] VA
C System Frequency:  60 [50][other] Hertz
2.3 Basic Requirements:

A Name Plate Rating:  Linear load, [60Hz][50Hz]
B Single-phase, common core construction.  Convection air cooled.  

C Insulation Class:  105°C system [130°C][180°C][other]
D Temperature Rise:  55°C [80°C][115°C][other]
E Standard impedance at 60Hz: 3.8% to 15.4% (up to 500VA), 2.1% to 5.9% (501VA to 1500VA) and 2.1% to 3.3% (1501VA to 2000VA).
F Transformer core construction: high grade, fully processed silicon steel laminations or better.
G Coil conductors: continuous copper windings, with soldered terminations.
H Impregnation: vacuum impregnated polyester resin.
I All units up to 2000VA have encapsulated coils encased in molded covers.
J Transformers up to 30A shall terminate in molded terminal block. Terminal block screw must incorporate standard SEMS captive washer and combination Phillips/slot screw.
K Transformers >30A shall terminate to 1/4-20 copper terminal lug. Screw to be 1/4-20 combination Phillips/slot screw. 
L Mounting Plate: standard heavy steel mounting plate or feet welded to core.

M Top Plate: standard heavy steel top plate welded to core, used for fuse block installation and grounding.
N Grounding Lug: all molded units will be supplied with green grounding screw and jumper link for the grounding of the secondary side and the core. 

O Secondary Fuse Kits: all molded units >100VA will be supplied with standard 13/32” x 1 ½”, midget/supplemental type fuse clips, with necessary voltage links and jumpers to also be supplied.

P Sound level to meet NEMA ST-20.
Q cULus listed, [CE Mark]
R Built to NEMA ST-1 and in accordance with all applicable UL, CSA and ANSI/IEEE standards.
Options:

· Class CC 13/32” x 1 ½”, 2-pole Fuse Block Holders.
· Midget/Supplemental Style 13/32” x 1 ½”, 1-pole Fuse Block Holder
· CE mark approved finger safe primary and secondary terminal covers for fused and non-fused transformers. 

· Lead kits for alternative termination.

2.4 Acceptable Product and Manufacturer:

A Molded machine tool rated control transformer by Hammond Power Solutions Inc. (Canada: 1-888-798-8882 / U.S.: 1-866-705-4684).
B Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.
3 EXECUTION

3.1 Installation
A Verify nameplate data.
B Check for damage and loose connections.
C Mount transformer to comply with all applicable codes.
D Coordinate all work in this section with all work of other sections.
E Prior to energizing transformer, verify primary and secondary voltages.
PAGE  
CSI-2004 (Section 26 22 13)                                  
                         Page 3 of 3                              
                                           SPS# 19, Rev: 02

