[image: image1.png]P
o w
E R
S O
1C IONS///,





Open Style General Purpose 

Industrial Control Transformer
Typical Specification
Canada
595 Southgate Drive

Guelph, Ontario
N1G 3W6
Phone: 1-888-798-8882
Fax: 1-519-822-9701
United States
1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

1 GENERAL
1.1 SCOPE

A This section defines open style, general purpose industrial control transformers as indicated.
B Transformers shall be designed, constructed and rated in accordance with NEMA ST-1, UL 5085-1 and UL5085-2, CSA C22.2 No. 66.1-06 and IEC 61558 standards. 

1.2 RELATED DOCUMENTS

A Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section

1.3 REFERENCES

A UL (ANSI/UL 5085-1 & ANSI/UL 5085-2)
B CSA (C22.2 No. 66.1-06)

C NEMA (ST-1) 

D IEC 61558-1 & IEC61558-2-2

1.4 SUBMITALS

A Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract. 

i Customer name, Customer location, and customer order number, shall identify all transmittals.

ii Product Data including VA rating, temperature rise, detailed dimensions, primary & secondary nominal voltages, primary & secondary voltage taps, inrush, unit weight, warranty.
1.5 STORAGE AND HANDLING

A Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations.
B Handle transformer using proper equipment for lifting and handling.

1.6 WARRANTY

A The transformer shall carry a 15 year limited pro-rated warranty.
(For details, refer to the manufacturers published warranty)
2 PRODUCTS
2.1 General construction:

A Single phase general purpose industrial control transformers shall be open style. All single phase transformers shall be constructed with copper wound coils and a single core. 
B Transformers shall be designed, constructed and rated in accordance with UL, CSA, NEMA and CE standards.

2.2 Voltage and VA Requirements:

A Primary & Secondary Voltage combinations: 
[600/480-120X240][600-120X240][600-24][240X480-120X240][380/347-120X240][380/347-24] [575/460/230-115/95][415/400/380-120/24][415/400/380-24][230X460-115][240X480-24] [575/460/400/230-115/95][347/277/240/208-120/24][277-120][208X416-120X240][208X416-24] [120X240-24][690-120X240][800-120X240][other] Volts
B VA Rating: [50][75][100][150][250][350][500][750][1000][1500][2000][3000][5000][other] VA
C System Frequency: [60][50][other] Hertz
2.3 Basic Requirements:
A Name Plate Rating:  Linear load, [60Hz][50Hz]
B Single-phase, common core construction. Convection air cooled  

C Insulation Class:  130°C system [180°C][other]
D Temperature Rise:  80°C [115°C][other]
E Transformer core construction: high grade, fully processed silicon steel laminations or better.
F Coil conductors: continuous copper windings, with terminations crimped and soldered.
G Impregnation: vacuum impregnated polyester resin and oven cured. 

H Sound level to meet NEMA ST-20

I Transformers up to 30A shall terminate in molded terminal block. Terminal block screw must incorporate standard SEMS captive washer and combination Phillips/slot screw.
J Transformers >30A shall terminate to 1/4-20 copper terminal lug. Screw to be 1/4-20 combination Phillips/slot screw. 
K UL listed, CSA approved.
L Built to NEMA ST-20 and in accordance with all applicable UL, CSA and ANSI/IEEE standards.
M Mounting Plate: standard heavy steel mounting feet welded to core.
N Necessary voltage links and jumpers to be supplied.
O Top Plate: standard heavy steel top plate welded to core, used for fuse block installation and grounding.

P Grounding Lug: all molded units will be supplied with green grounding screw and jumper link for the grounding of the secondary side and the core. 

Options:

· Secondary Fuse Kits: 13/32” x 1 ½”, midget/supplemental type fuse clips 

· Class CC 13/32” x 1 ½”, 2-pole Fuse Block Holders.

· Midget/Supplemental Style 13/32” x 1 ½”, 1-pole Fuse Block Holder

· Finger safe primary and secondary terminal covers for fused and non-fused transformers. 

2.4 Acceptable Product and Manufacturer:

A Open style, general purpose industrial control transformer by Hammond Power Solutions Inc. (Canada: 1-888-798-8882 / U.S.: 1-866-705-4684) Standard Products: Product must be standard item in manufacturer’s published catalog. 
B Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.
3 EXECUTION

3.1 Installation
A Verify nameplate data.
B Check for damage and loose connections.
C Mount transformer to comply with all applicable codes.
D Coordinate all work in this section with all work of other sections.
E Prior to energizing transformer, verify primary and secondary voltages 

PAGE  
CSI-2004 (Section 26 22 13)                                  
                         Page 1 of 3                              
                                           SPS# 20, Rev: 01

