1.2kV Class

Autotransformer

Typical Specification

Canada

595 Southgate Drive

Guelph, Ontario

N1G 3W6

Phone: 1-888-798-8882

Fax: 1-519-822-9701

United States

1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

- GENERAL

  - SCOPE

    - This section defines dry-type, enclosed & ventilated non-isolated Autotransformer as indicated.

  - RELATED DOCUMENTS

    - Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section

  - REFERENCES

    - ANSI C57.12.01/NEMA ST 20-Dry Type Transformer For General Applications

    - IEEE C57.110-1998

    - UL, CSA

  - SUBMITALS

    - Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract.

      - Customer name. Customer location and customer order number shall identify all transmittals.

      - Product Data including KVA rating, Temperature Rise, Detailed enclosure dimensions, Primary & Secondary nominal voltages, primary voltage taps, no load & full load losses per NEMA ST20, impedances, unit weight, warranty.

  - STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and if necessary, apply temporary heat where required to obtain suitable service conditions.

    - Handle transformer using proper equipment for lifting and handling, use when necessary lifting eye and/or brackets provided for that purpose.

  - WARRANTY

    - The transformer shall carry a 10 year limited warranty.

(For details, refer to the manufacturers published warranty)

- PRODUCTS

  - General construction:

    - Three phase autotransformers shall be either ventilated type or encapsulated. All three phases transformer shall be constructed with three winding and a single core. Convection air cooled.

    - Transformers shall be designed, constructed and rated in accordance with UL, CSA, and NEMA standards. If shipping to Europe, transformer will also have to be manufactured in accordance to CE standards and carry a CE mark.

    - Auto Transformers have no isolation from primary to secondary and the neutral (optional) is only a mid point and should not be grounded as a distribution isolated transformer.

    - If transformer is to be used for non-linear load applications, the transformer shall be derated as per ANSI/IEEE C57.110.

  - Voltage and kVA Requirements:

    - Primary Voltage:  [208][216][240][400][480][600][other] Volts

    - Secondary Voltage: [208][216][240][400][480][600][other] Volts

    - kVA Rating: [3][6][9][15][30][45][75][112.5][150][225][300][500][other] kVA

    - System Frequency:  60 [50][other] Hertz

  - Basic Requirements:

    - Standard impedance at 60Hz: 2% to 5% (up to 10kVA), 4% to 6.5% (above 10kVA)

    - Name Plate Rating:  Linear load, 60Hz

    - Insulation Class:  220°C system [200][other]

    - Temperature Rise:  150°C [130°C][115°C][80°C][other]

    - Core construction: high grade non-aging, fully processed silicon steel laminations or better.

    - Coil conductors: continuous aluminum [copper] windings, with terminations brazed, welded or bolted.

    - Impregnation: vacuum impregnated polyester resin.

    - Sound level to meet NEMA ST-20

    - Enclosure:  ventilated, NEMA 3R [NEMA 4][NEMA 4X][NEMA 12][other].

    - Enclosure Finish:  ANSI 61 Grey suitable for UL50 outdoor applications [other].

    - Transformers shall terminate in mounting pads. Mounting lugs will be included on all aluminum and copper units up to and including 270 amp ratings. Contractors shall provide all necessary lugs not already provided with transformer.

    - Anti-vibration pads/isolators shall be used between the transformer core and coil and the enclosure.

    - UL listed, CSA approved, [CE Mark]

    - Built to NEMA ST-20 and in accordance with all applicable UL, CSA and ANSI/IEEE standards

    - Ground core & coil assembly to enclosure with a flexible copper grounding strap or equivalent.

    - Mounting:

      - Ventilated units up to 750 lbs: Suitable for wall, floor or ceiling mounting (drip plate required)

      - Ventilated units over 750 lbs: Suitable for floor mounting only.

      - Encapsulated units up to 285 lbs: Suitable for wall or floor mounting.

      - Encapsulated units over 286 lbs: Suitable for floor mounting only.

    - Seismic Transformers shall be designed and seismically qualified according to the International Building Code (IBC) 2018, and the American Society of Civil Engineers ASCE 7-16 specifications.

Compliance must be demonstrated by testing.  (Applicable to floor mounted units only.)

Transformers can be designed to be approved for O.S.H.P.D California.

Options:

- Over-Temperature switches wired to internal terminal strip. Temperatures specified for use with class 220°C insulation systems. Standard configuration is N.C. opening on high temperature. Optional configuration is N.O. closing on high temperature. Installation options: [one switch: 170°C or 200°C on center coil][two switches: 170°C and 200°C on center coil][six switches: one 170°C and one 200°C on each of the 3 coils]

- TVSS

- Manufacturer has the ability to guarantee EMF levels as low as 10mG on the enclosure top and four sides from a distance of 1 meter for most units and kVA ranges. (Contact manufacturer for details on pricing and availability.)

- Load profile K-factor rated available.

- Voltage Taps

- Neutral Termination

- Vibration Isolators

- Low Sound [-3 dB][-5 dB][-8 dB]

- Strip Heaters

- Marine Duty (meet ABS requirements)

  - Acceptable Product and Manufacturer:

    - Hammond Power Solutions Inc. (Canada: 1-888-798-8882 / U.S.: 1-866-705-4684).

    - Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.

##### EXECUTION

  - Installation

    - The installing contractor shall install the Autotransformer per the manufacturer's recommended installation practices as found in the installation, operation, and maintenance manual and comply with all applicable codes.

    - Make sure that the transformer is level.

    - Check for damage and loose connections.

    - Mount transformer to comply with all applicable codes.

    - Install optional vibration isolation pads between transformer enclosure and the mounting surface.

    - Install seismic restraint where indicated on the drawing.

    - Coordinate all work in this section with all work of other sections.

    - Take Infrared Picture to verify connections accuracy or deficiencies.

    - Prior to energizing transformer, verify secondary voltages and if necessary adjust secondary taps.

    - Report for the Commission of the transformer shall include:

      - Primary & Secondary Voltages

      - Primary & secondary THDi & THDv