HPS Express L Line

1.2kV Class

Low Voltage Distribution Transformer

Typical Specification

| Mexico | Canada | United States |
| --- | --- | --- |
| Av. No. 800, Parque Industrial Guadalupe Guadalupe, NL, Mexico, C.P. 67190. Phone: (819) 690-8000 | 595 Southgate Drive Guelph, Ontario N1G 3W6 Phone: 1-888-798-8882 Fax: 1-519-822-9701 | 1100 Lake Street Baraboo, Wisconsin 53913-2866 Phone: 1-866-705-4684 Fax: 1-608-356-2452 |

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

- GENERAL

  - SCOPE

    - This section defines dry-type ventilated transformer as indicated.

  - RELATED DOCUMENTS

    - Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

  - REFERENCES

    - ANSI C57.12.01/NEMA ST-20 Dry-Type Transformer for General Applications

    - IEEE C57.110-1998

    - UL

  - SUBMITALS

    - Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract.

      - Customer name. Customer location and customer order number shall identify all transmittals.

      - Product Data including KVA rating, Temperature Rise, Detailed enclosure dimensions, Primary & Secondary nominal voltages, primary voltage taps, no load & full load losses per NEMA ST20, impedances, unit weight, warranty.

  - STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and if necessary, apply temporary heat where required to obtain suitable service conditions.

    - Handle transformer using proper equipment for lifting and handling; use when necessary lifting eye and/or brackets provided for that purpose.

  - WARRANTY

    - The transformer shall carry a 1 year limited warranty.

(For details, refer to the manufacturers published warranty)

- PRODUCTS

  - General construction:

    - Three phase transformers 9kVA and larger, shall be ventilated type. All three phase transformers shall be constructed with three windings and a single core. The primary side of each transformer shall, if applicable, be provided with taps that meet or exceed NEMA standards. Convection air cooled.

    - Transformers shall be designed, constructed and rated in accordance with UL and NEMA standards.

  - Voltage and kVA Requirements:

A. Primary Voltage:     Three Phase – 504/480/460/440/418Volts

B. Secondary Voltage: Three Phase - [220/127] Volts

C. kVA Rating:    Three Phase – [15][30][45][75][112.5][150][225][300][500] kVA

- System Frequency:  60 Hertz

  - Basic Requirements:

    - Standard impedance at 60Hz: 2% to 6.5%

    - Nameplate Rating:  Linear load, 60Hz

    - Insulation Class:  220°C system

    - Temperature Rise:  150°C

    - Taps:  504/480/460/440/418V

    - Core construction: high grade non-aging, fully processed silicon steel laminations or better.

    - Coil conductors: continuous aluminum windings, with terminations brazed, welded or bolted.

    - Impregnation: vacuum impregnated polyester resin.

    - Enclosure:  Type-2

    - Enclosure Finish:  ANSI 61 Grey.

    - Built to NEMA ST-20 and in accordance with all applicable UL and ANSI/IEEE standards.

    - Ground core & coil assembly to enclosure with a flexible copper grounding strap or equivalent.

    - Mounting:

      - Ventilated units up to 750 lbs: Suitable for wall, floor or ceiling mounting (drip plate required)

      - Ventilated units over 750 lbs.: Suitable for floor mounting only.

  - Acceptable Product and Manufacturer:

    - HPS Express L transformer, by: Hammond Power Solutions Inc. (Canada: 1-888-798-8882  /  U.S.: 1-866-705-4684)

    - Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.

##### EXECUTION

  - Installation

    - The installing contractor shall install the Low Voltage Distribution Transformer per the manufacturer's recommended installation practices as found in the installation, operation and maintenance manual and comply with all applicable codes.

    - Make sure that the transformer is level.

    - Check for damage and loose connections.

    - Mount transformer to comply with all applicable codes.

    - Install optional vibration isolation pads between transformer enclosure and the mounting surface.

    - Install seismic restraint where indicated on the drawing.

    - Coordinate all work in this section with all work of other sections.

    - Take Infrared Picture to verify connections accuracy or deficiencies.

    - Prior to energizing transformer, verify secondary voltages and if necessary adjust secondary taps.

    - Report for the Commission of the transformer shall include:

      - Primary & Secondary Voltages

      - Primary & Secondary THDi & THDv