1.2 kV Class

Vacuum Pressure Impregnation (VPI)

Dry-Type Grounding Transformer

Canada

595 Southgate Drive

Guelph, Ontario

N1G 3W6

Phone: 1-888-798-8882

Fax: 1-519-822-9701

United States

1100 Lake Street

Baraboo, Wisconsin

53913-2866

Phone: 1-866-705-4684

Fax: 1-608-356-2452

E-mail: sales@hammondpowersolutions.com

www.hammondpowersolutions.com

- GENERAL

  - SCOPE

    - This section defines dry-type, enclosed and ventilated 1.2kV Class low voltage grounding transformers as indicated.

    - Transformers shall be designed, constructed and rated in accordance with UL and NEMA and IEEEANSI standards.

  - RELATED DOCUMENTS

    - Drawing and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section

  - REFERENCES

    - NEMA ST-20 Dry-Type Transformer for General Applications

    - IEEE C57.110 Recommended Practice for establishing transformer capability when feeding non-sinusoidal load currents.

    - UL 1561, CSA C9-02 & C22.2 No. 47.

  - Energy Efficiency Levels

    - Grounding Transformers are exempt from:

      - DOE 2016 Low Voltage Energy Efficiency levels as per DOE 10 CFR Part 431 – effective Jan. 1, 2016.

      - NRCan 2019 effective as of April 30th, 2019 and ON Reg.404-12 – effective as of Jan. 1, 2018 (in Ontario)

  - TESTING & QUALITY CONTROL

A	Production tests: each unit according to:

- NEMA ST-20

- CSA C9 & C22.2 No. 47

B	Test each model design and submit report on request

C	Standard production tests to include:

- Applied potential test

- Induced voltage test

- Impedance voltage and load loss test

- Voltage ratio test

- No load and excitation current test

D	Additional type test should be made available on request include:

- Short circuit test

- BIL – basic impulse insulation level test

- Partial discharge test

- Sound level test

- Temperature rise test

  - SUBMITALS

    - Submit shop drawing and product data for approval and final documentation in the quantities listed according to the Conditions of the contract.

      - Customer name. Customer location and customer order number shall identify all transmittals.

      - Zig-Zag Autotransformer or Wye-Delta Transformer

      - Product Data including Neutral Current rating, Zero Sequence Impedance, Temperature Rise, BIL, Detailed enclosure dimensions, nominal voltages, no load & full load losses, impedances, unit weight, warranty.

  - STORAGE AND HANDLING

    - Store and handle in strict compliance with manufacturer’s instructions and recommendations. Protect from potential damage from weather and construction operations. Store so condensation will not form on or in the transformer housing and if necessary, apply temporary heat where required to obtain suitable service conditions.

    - Handle transformer using proper equipment for lifting and handling, use when necessary lifting eye and/or brackets provided for that purpose.

  - WARRANTY

    - The transformer shall carry a 1 year limited warranty.

(For details, refer to the manufacturers published warranty)

- PRODUCTS

  - General construction:

    - Transformer core shall be manufactured from quality non-aging, , fully processed silicon steel laminations. Cores are to be precisely cut to close tolerances to eliminate burrs and improve performance and low noise level. Cores are to be carefully assembled and rigidly held secure with structural steel clamps to minimize gaps.

    - Coils shall be designed for proper ventilation using [aluminum] [copper] conductors with insulated coil supports.  Coils shall be disc wound above 5 kV.

    - 220oC insulation systems based on Nomex® paper (or equivalent) shall provide long operating life and quiet operation.  The complete core and coil assembly shall be vacuum pressure impregnated with a polyester varnish and oven cured to make the assembly highly resistant to moisture, dust, and other industrial contaminants.  Insulation system shall be fire resistant and self extinguishing.

    - Transformers shall be designed, constructed and rated in accordance with UL, CSA, and NEMA standards. If shipping to Europe, transformer will carry a CE mark.

  - Voltage and rating Requirements:

    - System Voltage (Line to Line): ______ [Volts]

    - Primary Voltage (L-L) BIL Rating: ______(Kilovolts)

    - Neutral Voltage (L-N) BIL Rating: ______(Kilovolts)

    - Winding Configuration

    - Continuous Phase Rating: _____[Amperes]

    - Continuous Neutral Rating: _____ [Amperes

    - Fault Current Rating: ______[Amperes]

    - Fault Clearance Duration: _____[Seconds]

    - System Frequency:  _____  Hertz

Zero Sequence Impedance: ______ [Ohms]

  - Key Requirements:

    - The manufacturer will provide third party test results verifying short circuit capability on the standard design construction concept used by the manufacturer.

    - The following production tests must be completed on all transformers. Pass fail criteria will be per ANSI C57.12.01 and C57.12.91.

      - Polarity

      - Ratio

      - Resistance of coils

      - Insulation resistance test

      - Power frequency voltage-withstand tests on each winding.

      - Induced voltage test

      - No load loss

      - Load loss

      - Impedance test

  - Basic Requirements:

    - Insulation Class:  220°C system [200][other]

    - Temperature Rise:  Average winding rise by resistance shall not exceed 150 °C [115°C] [80°C] [other] in an average 30°C and a maximum 40°C ambient.

    - Three-phase, common core construction. Convection air cooled

    - Impregnation: Vacuum pressure impregnated (VPI) polyester resin.

    - Sound level to meet NEMA ST-20:2014

    - Enclosure:  Ventilated [NEMA 3R][NEMA 3R Enhanced c/w filters][Totally Enclosed Type 12] [Totally Enclosed Type 4][Core and Coil][other].

    - Enclosure Finish:  [ANSI 61 Grey] [ANSI 61 Grey suitable for UL50 outdoor applications] [ANSI 49][other].

    - Anti-vibration pads/isolators shall be used between the transformer core and coil and the enclosure.

    - Seismic: Transformers shall be designed and seismically qualified according to the International Building Code (IBC) 2018, and the American Society of Civil Engineers ASCE 7-16 specifications.

Compliance must be demonstrated by testing.  (Applicable to floor mounted units only.)

Transformers can be designed to be approved for O.S.H.P.D California.

    - Transformers shall terminate in mounting pads or mechanical lugs. Primary and secondary terminations are to have terminals on the same side of the transformer mounted on separate insulated supports, with the HV terminations in the upper half of the enclosure and LV terminations in the lower half.  Mechanical type lugs shall be included on primary, secondary and neutral customer terminations on all aluminum and copper units up to and including 270 amp ratings. Contractors shall provide all necessary lugs not already provided with transformer.

    - Anti-vibration pads/isolators shall be used between the transformer core and coil and the enclosure.

Options:

- Vibration Isolators

- Low Sound level: [-3 dB], [-5 dB], [-8 dB], [other]

- Enclosures: [Type 3R – Stainless Steel], [Type 3R – Enhanced], [Type 4], [Type 4X Stainless Steel], [Type 12], [other]

- Over-Temperature switches wired to internal terminal strip. Temperatures specified for use with class 220°C insulation systems. Standard configuration is N.C. opening on high temperature. Optional configuration is N.O. closing on high temperature. Installation options: [one switch: 170°C or 200°C on center coil], [two switches: 170°C and 200°C on center coil], [six switches: one 170°C and one 200°C on each of the 3 coils].

- Strip Heater

- Marine Duty (meet ABS requirements)

- SPD (Surge Protection Device)

  - Acceptable Product and Manufacturer:

    - Hammond Power Solutions Inc. (USA 1800-537-0500).

    - Hammond Power Solutions Inc. (Canada: 1-888-798-8882).

    - Substitutions are permitted, subject to meeting all requirements of this specification and also having written approval by engineering 10 days prior to bid closing.

##### EXECUTION

  - Installation

    - The installing contractor shall install the Dry-Type Low Voltage  Transformer per the manufacturer's recommended installation practices as found in the installation, operation, and maintenance manual and comply with all applicable codes.

    - Make sure that the transformer is level.

    - The transformer shall be mounted on a concrete pad unless otherwise indicated.

    - Check for damage and loose connections.

    - Mount transformer on suitable isolation pad to minimize vibrations.

    - Install seismic restraint where indicated on the drawing.

    - Coordinate all work in this section with all work of other sections.

    - Take Infrared Picture to verify connections accuracy or deficiencies.

    - Prior to energizing transformer, verify secondary voltages and if necessary adjust secondary taps.